## Slide 1
GridPilot: Real-Time Grid-Responsive Control for AI Supercomputers
Three control layers + an isolated 'safety island' that bypasses slow software for fast grid response.
Tier 3
Tier 2
Tier 1
Hardware
Cluster operating-point selector (hourly)
Picks a target IT power that meets the grid commitment
at the meter --- includes the cooling-overhead correction.
Per-host coordinator (1 Hz)
Predicts workload power one second ahead;
splits the host envelope across GPUs.
Per-GPU power-cap loop (200 Hz)
Standard PID; tracks the assigned per-GPU power target
via the NVIDIA Management Library.
GPU silicon + facility cooling
Power swings settle on the GPU board within ~20 ms;
facility meter reflects them within ~90 ms total.
Electricity grid
frequency event
Safety island
(real-time C bypass)
Reads the grid trigger and pushes a new GPU power cap
directly --- skipping the slower software path.
trigger (UDP)
~ 97 ms median
Measured end-to-end response: 97 ms median (101 ms worst case across 90 trials) --- about 7x faster than the Nordic Fast Frequency Reserve 700 ms budget.
Acronyms used in this slide: PID = Proportional-Integral-Derivative controller · GPU = Graphics Processing Unit · PUE = Power Usage Effectiveness · FFR = Fast Frequency Reserve. Diagram is illustrative; the controller is open-source under MIT.